## README
KINGSWALK SCADA — SLD Field Map Workbook
Companion workbook to SPEC.md — ground truth for every asset, field, protocol and IP address.
# | Sheet | Purpose | Row count
1 | Item Inventory | Per-item list of all 104 outgoing DBs across MB 1.1–5.3 with DB code, tenant, area, rating, MP code, breaker type code and cable. Extracted from per-MB schematics 301–309 (authoritative). | 104 items
2 | Measuring Packages | MP1–MP7 legend decomposed into one row per individual function (measurement, trending, energy, statistic, waveform, PQ index, protection). Colour-banded by MP. | 48 functions
3 | Breaker Specs | Drawing shorthand → ABB family mapping (TM3 = ACB-TMAX3, TS2 = MCCB-EMAX-XTS2, TS1 = anomaly). | 3 codes
4 | MP Function Catalog | Alternate sortable/filterable view of the 48 MP functions with ANSI codes, polling frequencies and suggested DB field names for the ingest layer. | 48 functions
5 | Network & Protocol Plan | Per-device IP address, subnet mask, gateway, VLAN, protocol (Modbus TCP / IEC 61850), port and Modbus Unit ID for every Ekip trip unit, Ekip Com gateway and M4M 30 analyzer. | ~150 rows
6 | Gaps & Actions | Open items: breaker / MP / naming discrepancies, protocol confirmations, VLAN & cabling gaps, IP scheme sign-off. | 21+ gaps
Authoritative sources
| Drawing 643.E.300 | Tenant list / areas / cable sizes (overview, 114 rows)
| Drawings 643.E.301–309 | Per-MB schematics — source of truth for MP code, breaker type code and per-item rating
| SPEC.md §3 / §6.4 | Site overview, standard MB architecture, network & protocol addressing scheme
| db/migrations/0001_initial.sql | Runnable PostgreSQL + TimescaleDB migration for the initial schema

## Item Inventory
KINGSWALK — SLD Item Inventory (per-MB authoritative)
One row per outgoing DB on drawings 643.E.301–309. Ratings, MP codes and breaker type codes come from the per-MB schematics (authoritative). Tenant names, areas and cable sizes are cross-referenced from drawing 643.E.300.
Main Board | Drawing | DB Code | Tenant / Service | Area (m²) | Rating | MP Code | Breaker Code | Cable | Notes
MB 1.1 | 643.E.301 | DB-17 | PEP CELL | 56.81 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 1.1 | 643.E.301 | DB-17A | KING PIE | 61.03 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 1.1 | 643.E.301 | DB-17B | MR PRICE CELL | 50.44 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 1.1 | 643.E.301 | DB-18 | SHOPRITE | 2716.13 | 800A TP | MP2 | TS2 | 4 x 4C x 120mm² ALU CABLES | Anchor / bulk feeder
MB 1.1 | 643.E.301 | DB-19 | TRUWORTHS | 922.22 | 200A TP | MP2 | TM3 | 4C x 120mm² ALU CABLES
MB 1.1 | 643.E.301 | DB-20/21 | IDENTITY / SYNC | 332.36 | 200A TP | MP2 | TM3 | 4C x 70mm² ALU CABLE
MB 1.1 | 643.E.301 | DB-22/23 | JET | 842.63 | 200A TP | MP2 | TM3 | 4C x 120mm² ALU CABLES
MB 1.1 | 643.E.301 | DB-24 | SPORTSCENE | 401.98 | 120A TP | MP2 | TM3 | 4C x 70mm² ALU CABLE
MB 1.1 | 643.E.301 | DB-24A | MARKHAMS | 352.61 | 120A TP | MP2 | TM3 | 4C x 70mm² ALU CABLE
MB 1.1 | 643.E.301 | DB-26 |  |  | 120A TP | MP2 | TM3
MB 2.1 | 643.E.302 | DB-05 | BOXER | 1809.27 | 600A TP | MP2 | TS2 | 3 x 4C x 120mm² ALU CABLES | Anchor / bulk feeder
MB 2.1 | 643.E.302 | DB-08 | PEP | 501.52 | 150A TP | MP2 | TM3 | 4C x 95mm² ALU CABLE
MB 2.1 | 643.E.302 | DB-08A | SENZA | 40 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 2.1 | 643.E.302 | DB-09 | VACANT | 151.83 | 80A TP | MP2 | TM3 | 4C x 35mm² ALU CABLE
MB 2.1 | 643.E.302 | DB-10 | VACANT | 148.12 | 80A TP | MP2 | TM3 | 4C x 35mm² ALU CABLE
MB 2.1 | 643.E.302 | DB-11 | VACANT | 201.91 | 80A TP | MP2 | TM3 | 4C x 35mm² ALU CABLE
MB 2.1 | 643.E.302 | DB-11A | CLOTHING JUNCTION | 229.35 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 2.1 | 643.E.302 | DB-12 | JAM | 357.48 | 120A TP | MP2 | TM3 | 4C x 70mm² ALU CABLE
MB 2.2 | 643.E.303 | DB-01 | VACANT | 131.50 | 80A TP | MP2 | TM3 | 4C x 35mm² ALU CABLE
MB 2.2 | 643.E.303 | DB-01A | WATLOO | 800.25 | 200A TP | MP2 | TS2 | 4C x 120mm² ALU CABLE | Anchor / bulk feeder
MB 2.2 | 643.E.303 | DB-01B | KINGSLEY BEVERAGES | 250.67 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 2.2 | 643.E.303 | DB-01C | KIT KAT | 472.30 | 120A TP | MP2 | TM3 | 4C x 70mm² ALU CABLE
MB 2.2 | 643.E.303 | DB-01D | CAPITEC ATM | 28.52 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 2.2 | 643.E.303 | DB-02 | VACANT | 150.49 | 80A TP | MP2 | TM3 | 4C x 35mm² ALU CABLE
MB 2.2 | 643.E.303 | DB-03 | MAX BOX | 50.20 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 2.2 | 643.E.303 | DB-03A | ACKERMANS CONNECT | 52.13 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 2.2 | 643.E.303 | DB-04 | PIE FACTORY | 41.23 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 2.3 | 643.E.304 | DB-13/14 | VACANT | 682.41 | 200A TP | MP2 | TM3 | 4C x 120mm² ALU CABLE
MB 2.3 | 643.E.304 | DB-15 | CLICKS | 802.76 | 200A TP | MP2 | TM3 | 4C x 120mm² ALU CABLES
MB 2.3 | 643.E.304 | DB-16 | SHOPRITE LIQUOR | 252.08 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-74 | SPUR | 355.31 | 150A TP | MP2 | TM3 | 4C x 95mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-75 | KFC | 201.83 | 150A TP | MP2 | TM3 | 4C x 95mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-76 | STEERS & DEBONAIRS | 273.55 | 150A TP | MP2 | TM3 | 4C x 95mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-77 | ROCOMAMA'S | 275.80 | 150A TP | MP2 | TM3 | 4C x 95mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-78 | CONVERSE | 112.34 | 80A TP | MP2 | TM3 | 4C x 35mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-78A | CAPITEC ATM | 10.06 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-80 | VACANT | 79.48 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-80A | SPECSAVERS | 74.41 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-81 | VACANT | 52.85 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-82 |  |  | 80A TP | MP2 | TM3
MB 3.1 | 643.E.305 | DB-83 |  |  | 100A TP | MP2 | TM3
MB 3.1 | 643.E.305 | DB-84 |  |  | 100A TP | MP2 | TM3
MB 3.1 | 643.E.305 | DB-85 |  |  | 80A TP | MP2 | TM3
MB 3.1 | 643.E.305 | DB-86 |  |  | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-86A | POWER FASHION | 307.18 | 120A TP | MP2 | TM3 | 4C x 70mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-87 |  |  | 100A TP | MP2 | TM3
MB 3.1 | 643.E.305 | DB-88 |  |  | 100A TP | MP2 | TM3
MB 3.1 | 643.E.305 | DB-89 |  |  | 80A TP | MP2 | TM3
MB 3.1 | 643.E.305 | DB-89A | NEDBANK ATM | 10.06 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-89B | CAKE ZONE | 56.30 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-89C | VACANT | 55.79 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-90 | CASH CRUSADERS | 251.38 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-92 | ABSA | 231.77 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 3.1 | 643.E.305 | DB-SR1 | STORE ROOM 1 | 11.11 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 4.1 | 643.E.306 | DB-46 | FNB | 252.38 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 4.1 | 643.E.306 | DB-47 | STANDARD BANK | 221.46 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 4.1 | 643.E.306 | DB-48 | VACANT | 65.55 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 4.1 | 643.E.306 | DB-48A | ATM | 11.71 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 4.1 | 643.E.306 | DB-48B | VACANT | 59.95 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 4.1 | 643.E.306 | DB-48C | VACANT | 104.72 | 80A TP | MP2 | TM3 | 4C x 35mm² ALU CABLE
MB 4.1 | 643.E.306 | DB-52A | PEP HOME | 271.11 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 4.1 | 643.E.306 | DB-53 | MR PRICE & KIDS | 613.09 | 200A TP | MP2 | TM3 | 4C x 120mm² ALU CABLE
MB 4.1 | 643.E.306 | DB-54 | TEKKIE TOWN | 279.70 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 4.1 | 643.E.306 | DB-55 |  |  | 120A TP | MP2 | TM3
MB 4.1 | 643.E.306 | DB-57 |  |  | 200A TP | MP2 | TM3
MB 4.1 | 643.E.306 | DB-58/59 |  |  | 120A TP | MP2 | TM3
MB 4.1 | 643.E.306 | DB-60 |  |  | 120A TP | MP2 | TM3
MB 4.1 | 643.E.306 | DB-62 |  |  | 80A TP | MP2 | TM3 | 4C x 35mm² ALU CABLE
MB 4.1 | 643.E.306 | DB-64 | VACANT | 618.94 | 200A TP | MP2 | TM3 | 4C x 120mm² ALU CABLE
MB 4.1 | 643.E.306 | DB-66 |  |  | 80A TP | MP2 | TM3
MB 4.1 | 643.E.306 | DB-66A |  |  | 60A TP | MP2 | TM3
MB 4.1 | 643.E.306 | DB-67 |  |  | 80A TP | MP2 | TM3
MB 4.1 | 643.E.306 | DB-67A | VACANT | 50 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 4.1 | 643.E.306 | DB-68 | ROMANS PIZZA | 124.91 | 150A TP | MP2 | TM3 | 4C x 95mm² ALU CABLE
MB 4.1 | 643.E.306 | DB-69 | HUNGRY LION | 145.54 | 150A TP | MP2 | TM3 | 4C x 95mm² ALU CABLE
MB 4.1 | 643.E.306 | DB-70 | PANAROTTIS | 339.23 | 150A TP | MP2 | TM3 | 4C x 95mm² ALU CABLE
MB 5.1 | 643.E.307 | DB-38 | PnP LIQUOR | 306.01 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 5.1 | 643.E.307 | DB-38A | CRAZY STORE | 251.53 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 5.1 | 643.E.307 | DB-39 | PICK n PAY | 2445.43 | 200A TP | MP2 | TS1 | 3 x 4C x 120mm² ALU CABLE | ⚠ TS1 not in legend — confirm
MB 5.1 | 643.E.307 | DB-DOMESTIC | DOMESTIC PUMP ROOM |  | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 5.1 | 643.E.307 | DB-FIRE | FIRE PUMP ROOM |  | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 5.1 | 643.E.307 | DB-SR2 | STORE ROOM 2 | 42.73 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 5.2 | 643.E.308 | DB-40 | VACANT | 65.95 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 5.2 | 643.E.308 | DB-40A | VACANT | 65.95 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 5.2 | 643.E.308 | DB-41 | TORGA OPTICAL | 62.19 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 5.2 | 643.E.308 | DB-42 | AMERICAN SWISS | 60.03 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 5.2 | 643.E.308 | DB-43 | OLD MUTUAL | 216.94 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 5.2 | 643.E.308 | DB-44 | CAPITEC | 275.29 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 5.2 | 643.E.308 | DB-44A | MOJO | 304.08 | 120A TP | MP2 | TM3 | 4C x 70mm² ALU CABLE
MB 5.2 | 643.E.308 | DB-45 | BRADLOWS | 329.93 | 120A TP | MP2 | TM3 | 4C x 70mm² ALU CABLE
MB 5.2 | 643.E.308 | DB-45A | VACANT | 446.06 | 120A TP | MP2 | TM3 | 4C x 70mm² ALU CABLE
MB 5.2 | 643.E.308 | DB-93 |  |  | 200A TP | MP2 | TM3
MB 5.3 | 643.E.309 | DB-27/28 | TOTALSPORTS | 381.34 | 120A TP | MP2 | TM3 | 4C x 70mm² ALU CABLE
MB 5.3 | 643.E.309 | DB-29 | VACANT | 287.09 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 5.3 | 643.E.309 | DB-30 | LEGIT | 251.80 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 5.3 | 643.E.309 | DB-31 | JOHN GRAIG | 211.80 | 100A TP | MP2 | TM3 | 4C x 50mm² ALU CABLE
MB 5.3 | 643.E.309 | DB-32 | VACANT | 187.76 | 80A TP | MP2 | TM3 | 4C x 35mm² ALU CABLE
MB 5.3 | 643.E.309 | DB-32A | CODE | 152.07 | 80A TP | MP2 | TM3 | 4C x 35mm² ALU CABLE
MB 5.3 | 643.E.309 | DB-33 | REFINERY | 162.03 | 80A TP | MP2 | TM3 | 4C x 35mm² ALU CABLE
MB 5.3 | 643.E.309 | DB-34 | VOLPES | 451.62 | 120A TP | MP2 | TM3 | 4C x 70mm² ALU CABLE
MB 5.3 | 643.E.309 | DB-36 | ARTHUR FORD | 50.24 | 60A TP | MP2 | TM3 | 4C x 25mm² ALU CABLE
MB 5.3 | 643.E.309 | DB-37 |  |  | 200A TP | MP2 | TM3
MB 5.3 | 643.E.309 | DB-CM |  |  | 80A TP | MP2 | TM3
MB 5.3 | 643.E.309 | DB-SEC |  |  | 60A TP | MP2 | TM3

## Measuring Packages
KINGSWALK — Single Line Diagram Codes: Measuring Packages
Source: 'SINGLE LINE DIAGRAM CODES' legend on drawings 643.E.301–309. Each package is decomposed into one row per individual function (measurement, trending, energy, statistic, waveform, power-quality index, protection). These are the signals the GUI must expose per asset.
MP | Function Group / Kit | Function | Abbreviation / ANSI | Unit | Description
MP1 | Basic Measurement (baseline) Kit: Ekip Measuring (built-in) | Phase-to-Phase Voltage | V_LL | V | RMS voltage between each pair of phases (L1-L2, L2-L3, L3-L1).
|  | Phase-to-Neutral Voltage | V_LN | V | RMS voltage between each phase and the neutral conductor.
|  | Phase Sequence | PhSeq | L1-L2-L3 | Rotational sequence of the three-phase system; alarms on reversal.
|  | Frequency | f | Hz | Fundamental system frequency (nominal 50 Hz).
|  | Active Power | P | kW | Real power delivered to the load.
|  | Reactive Power | Q | kVAr | Reactive power component of the load.
|  | Apparent Power | S | kVA | Vector sum of active and reactive power.
|  | Power Factor | PF / cosφ | — | Ratio P/S; sign indicates leading or lagging.
|  | Line Currents | I_L1 / I_L2 / I_L3 | A | RMS current in each phase conductor.
|  | Neutral Current | I_N | A | RMS current in the neutral conductor (unbalance / harmonic return indicator).
|  | Peak (Crest) Factor | CF | — | Ratio of peak-to-RMS current — harmonic distortion indicator.
MP2 | Data Logger (MP1 + trending + energy + events) Kit: Ekip Com + Datalogger module | Trending — Voltage | V trend | V | Time-stamped rolling log of all voltage channels.
|  | Trending — Current | I trend | A | Time-stamped rolling log of line and neutral currents.
|  | Trending — Active Power | P trend | kW | Time-stamped rolling log of total active power.
|  | Trending — Reactive Power | Q trend | kVAr | Time-stamped rolling log of total reactive power.
|  | Trending — Apparent Power | S trend | kVA | Time-stamped rolling log of total apparent power.
|  | Trending — Power Factor | PF trend | — | Time-stamped rolling log of system power factor.
|  | Trending — THD | THD trend | % | Time-stamped log of voltage and current total harmonic distortion.
|  | Active Energy Counter | Ea | kWh | Cumulative kWh — billing and monthly usage reports.
|  | Reactive Energy Counter | Er | kVArh | Cumulative kVArh — reactive-energy billing.
|  | Min / Max / Avg Logging | Stats | per-metric | Per-interval statistical envelope for every measured value.
|  | Event Buffer | Events | event | FIFO buffer of state changes, alarms and trips with sub-cycle timestamps.
MP3 | Network Analyzer (full power quality) Kit: M4M 30 or Ekip Power Controller | Voltage Waveform Capture | V waveform | samples | Oscilloscope-grade voltage capture on trigger or schedule.
|  | Current Waveform Capture | I waveform | samples | Oscilloscope-grade current capture, synchronised with voltage.
|  | Harmonic Analysis — up to 50th | H1..H50 | % of fund. | Magnitude of each harmonic order up to the 50th (V and I).
|  | Voltage THD | THD-V | % | EN 50160 compliance metric.
|  | Current THD | THD-I | % | IEEE 519 compliance metric.
|  | Individual Harmonic Levels | Hn | % | Per-harmonic value table driving the GUI harmonic-bar chart.
|  | Voltage Unbalance | VU | % | Negative-sequence unbalance factor (EN 50160 ≤ 2%).
|  | Flicker (Pst / Plt) | Pst / Plt | — | Short- (10 min) and long-term (2 h) flicker severity per EN 61000-4-15.
MP4 | Voltage Protections Kit: Ekip Voltage protection module | Over-voltage | OV (ANSI 59) | V | Trips when any phase voltage exceeds the configured threshold.
|  | Under-voltage | UV (ANSI 27) | V | Trips when any phase voltage drops below the configured threshold.
|  | Voltage Unbalance Protection | VU prot | % | Trips on sustained voltage unbalance exceeding the configured limit.
|  | Residual / Zero-sequence Voltage | V0 (ANSI 59N) | V | Detects earth fault via zero-sequence voltage, where sensing is fitted.
MP5 | Frequency Protections Kit: Ekip Frequency protection module | Over-frequency | OF (ANSI 81O) | Hz | Trips when frequency exceeds the upper limit (typically 51.5 Hz).
|  | Under-frequency | UF (ANSI 81U) | Hz | Trips when frequency falls below the lower limit (typically 47.5 Hz).
|  | Rate-of-Change of Frequency | df/dt (ANSI 81R) | Hz/s | Anti-islanding / loss-of-mains detection where the trip unit supports it.
MP6 | Power Protections Kit: Ekip Power protection module | Directional Reverse Power | RP (ANSI 32R) | kW | Trips on reverse active power flow — used on generator incomers.
|  | Power-factor Protection | cosφ (ANSI 55) | — | Trips when power factor falls below (or above) the configured limit.
|  | Directional Active Power | D (ANSI 32) | kW | Directional active power protection for fault discrimination.
|  | Reverse Reactive Power | RQ | kVAr | Trips on reverse reactive power flow.
|  | Over Reactive Power | OQ | kVAr | Trips when reactive power demand exceeds configured limit.
|  | Over Active Power | OP | kW | Trips when active power demand exceeds configured limit.
|  | Under Active Power | UP | kW | Trips on loss-of-load (active power below threshold).
|  | Second-stage Reverse Reactive | 2RQ | kVAr | Escalated second stage of reverse reactive trip.
MP7 | Differential / Residual (S(V) family) Kit: Ekip G (earth-fault) + Rc module | Earth-fault stage 1 | S(V) (ANSI 50G/51N) | A | First-stage earth-fault via residual current or voltage sensing.
|  | Earth-fault stage 2 | S(V)2 | A | Faster second stage of earth-fault for severe faults.
|  | Residual-Current (Earth Leakage) | R (ANSI 87N / Rc) | mA | True residual-current protection via ABB Ekip Rc module.
⚠ Note | Every outgoing on drawings 301–309 is tagged MP2. MP3–MP7 are declared in the legend but only assigned to main incomers and upstream isolators. Confirm with client whether specific tenant feeds (e.g. anchors with VFD loads) should additionally carry MP3 harmonic monitoring before procurement. TS1 tagged on DB-39 (MB 5.1) is anomalous — see Breaker Specs sheet.

## Breaker Specs
KINGSWALK — Breaker Type Codes (SLD shorthand)
Source: 'SINGLE LINE DIAGRAM CODES' legend on drawings 643.E.301–309. Each outgoing is tagged with one code in the MP / breaker-code strip directly below the rating row.
Code | Drawing legend text | Interpretation (ABB family) | Typical Use | Notes
TM3 | ACB-TMAX3 | Tmax XT moulded-case breaker with Ekip trip unit, frame 3 | Tenant DB outgoing feeders | Drawings 301–309 apply TM3 to every tenant feed except the large anchors. Ratings observed: 60, 80, 100, 120, 150, 160, 200A TP. Trip unit must support the MP2 Data Logger package (Ekip LSIG + Datalogger).
TS2 | MCCB-EMAX-XTS2 | Emax 2 air circuit breaker, larger frame (S2-class) | Anchor tenants / bulk feeders | Drawing 301 applies TS2 to DB-18 SHOPRITE (800A TP). Drawing 302 applies TS2 to DB-05 BOXER (600A TP). Drawing 303 uses TS2 on DB-01A WATERLOO (200A TP). TS2 also appears on the MB 1.1 incoming isolator (1600A TP). Trip unit must support MP2; where the feed is also metered for bulk tariff, an additional M4M 30 analyzer is fitted.
TS1 | (abbreviated — confirm with client) | Smaller Emax frame / larger XT frame (exact model TBC) | Observed on DB-39 PICK n PAY (200A TP, MB 5.1) — ONE instance only | Only ONE instance of TS1 across all drawings 301–309 — drawing 307 (MB 5.1), DB-39 PICK n PAY, 200A TP. The SLD legend block on drawing 307 does NOT include a TS1 entry, so this is either a typo for TS2/TM3 or a one-off. RAISED AS GAP GAP-16 — client confirmation required before procurement.

## MP Function Catalog
KINGSWALK — MP Function Catalog (DB schema reference)
Flat sortable/filterable view of every MP signal with ANSI codes, polling frequencies and suggested DB field names. Use this as the column reference when building the measurements / events / protection_settings tables.
# | MP | Function / Signal | Abbreviation | ANSI | Category | Unit | Polling / Capture | Suggested DB field | Description
1 | MP1 | Phase-to-Phase Voltage | V_LL | — | Measurement | V | 1 s | v_ll_l12,v_ll_l23,v_ll_l31 | RMS voltage between each pair of phases (L1-L2, L2-L3, L3-L1).
2 | MP1 | Phase-to-Neutral Voltage | V_LN | — | Measurement | V | 1 s | v_ln_l1,v_ln_l2,v_ln_l3 | RMS voltage between each phase and the neutral conductor.
3 | MP1 | Phase Sequence | PhSeq | — | Measurement | L1-L2-L3 | On change | phase_sequence | Rotational sequence of the three-phase system; alarms on reversal.
4 | MP1 | Frequency | f | — | Measurement | Hz | 1 s | frequency_hz | Fundamental system frequency (nominal 50 Hz).
5 | MP1 | Active Power | P | — | Measurement | kW | 1 s | active_power_kw | Real power delivered to the load.
6 | MP1 | Reactive Power | Q | — | Measurement | kVAr | 1 s | reactive_power_kvar | Reactive power component of the load.
7 | MP1 | Apparent Power | S | — | Measurement | kVA | 1 s | apparent_power_kva | Vector sum of active and reactive power.
8 | MP1 | Power Factor | PF / cosφ | — | Measurement | — | 1 s | power_factor | Ratio P/S; sign indicates leading or lagging.
9 | MP1 | Line Currents | I_L1 / I_L2 / I_L3 | — | Measurement | A | 1 s | i_l1,i_l2,i_l3 | RMS current in each phase conductor.
10 | MP1 | Neutral Current | I_N | — | Measurement | A | 1 s | i_n | RMS current in the neutral conductor (unbalance / harmonic return indicator).
11 | MP1 | Peak (Crest) Factor | CF | — | Measurement | — | 1 s | crest_factor | Ratio of peak-to-RMS current — harmonic distortion indicator.
12 | MP2 | Trending — Voltage | V trend | — | Trending | V | 15 min | ts_v_history | Time-stamped rolling log of all voltage channels.
13 | MP2 | Trending — Current | I trend | — | Trending | A | 15 min | ts_i_history | Time-stamped rolling log of line and neutral currents.
14 | MP2 | Trending — Active Power | P trend | — | Trending | kW | 15 min | ts_p_history | Time-stamped rolling log of total active power.
15 | MP2 | Trending — Reactive Power | Q trend | — | Trending | kVAr | 15 min | ts_q_history | Time-stamped rolling log of total reactive power.
16 | MP2 | Trending — Apparent Power | S trend | — | Trending | kVA | 15 min | ts_s_history | Time-stamped rolling log of total apparent power.
17 | MP2 | Trending — Power Factor | PF trend | — | Trending | — | 15 min | ts_pf_history | Time-stamped rolling log of system power factor.
18 | MP2 | Trending — THD | THD trend | — | Trending | % | 15 min | ts_thd_history | Time-stamped log of voltage and current total harmonic distortion.
19 | MP2 | Active Energy Counter | Ea | — | Energy | kWh | Continuous | energy_active_kwh | Cumulative kWh — billing and monthly usage reports.
20 | MP2 | Reactive Energy Counter | Er | — | Energy | kVArh | Continuous | energy_reactive_kvarh | Cumulative kVArh — reactive-energy billing.
21 | MP2 | Min / Max / Avg Logging | Stats | — | Statistics | per-metric | Per interval | stats_min_max_avg | Per-interval statistical envelope for every measured value.
22 | MP2 | Event Buffer | Events | — | Events | event | On event | event_log | FIFO buffer of state changes, alarms and trips with sub-cycle timestamps.
23 | MP3 | Voltage Waveform Capture | V waveform | — | Waveform | samples | On trigger | waveform_v | Oscilloscope-grade voltage capture on trigger or schedule.
24 | MP3 | Current Waveform Capture | I waveform | — | Waveform | samples | On trigger | waveform_i | Oscilloscope-grade current capture, synchronised with voltage.
25 | MP3 | Harmonic Analysis — up to 50th | H1..H50 | — | Power Quality | % of fund. | 1 min | harmonics_v,harmonics_i | Magnitude of each harmonic order up to the 50th (V and I).
26 | MP3 | Voltage THD | THD-V | — | Power Quality | % | 1 min | thd_v | EN 50160 compliance metric.
27 | MP3 | Current THD | THD-I | — | Power Quality | % | 1 min | thd_i | IEEE 519 compliance metric.
28 | MP3 | Individual Harmonic Levels | Hn | — | Power Quality | % | 1 min | harmonics_detail | Per-harmonic value table driving the GUI harmonic-bar chart.
29 | MP3 | Voltage Unbalance | VU | — | Power Quality | % | 1 min | voltage_unbalance | Negative-sequence unbalance factor (EN 50160 ≤ 2%).
30 | MP3 | Flicker (Pst / Plt) | Pst / Plt | — | Power Quality | — | 10 min / 2 h | flicker_pst,flicker_plt | Short- (10 min) and long-term (2 h) flicker severity per EN 61000-4-15.
31 | MP4 | Over-voltage | OV (ANSI 59) | 59 | Protection | V | Protection cycle | prot_ov | Trips when any phase voltage exceeds the configured threshold.
32 | MP4 | Under-voltage | UV (ANSI 27) | 27 | Protection | V | Protection cycle | prot_uv | Trips when any phase voltage drops below the configured threshold.
33 | MP4 | Voltage Unbalance Protection | VU prot | — | Protection | % | Protection cycle | prot_vu | Trips on sustained voltage unbalance exceeding the configured limit.
34 | MP4 | Residual / Zero-sequence Voltage | V0 (ANSI 59N) | 59N | Protection | V | Protection cycle | prot_v0 | Detects earth fault via zero-sequence voltage, where sensing is fitted.
35 | MP5 | Over-frequency | OF (ANSI 81O) | 81O | Protection | Hz | Protection cycle | prot_of | Trips when frequency exceeds the upper limit (typically 51.5 Hz).
36 | MP5 | Under-frequency | UF (ANSI 81U) | 81U | Protection | Hz | Protection cycle | prot_uf | Trips when frequency falls below the lower limit (typically 47.5 Hz).
37 | MP5 | Rate-of-Change of Frequency | df/dt (ANSI 81R) | 81R | Protection | Hz/s | Protection cycle | prot_dfdt | Anti-islanding / loss-of-mains detection where the trip unit supports it.
38 | MP6 | Directional Reverse Power | RP (ANSI 32R) | 32R | Protection | kW | Protection cycle | prot_rp | Trips on reverse active power flow — used on generator incomers.
39 | MP6 | Power-factor Protection | cosφ (ANSI 55) | 55 | Protection | — | Protection cycle | prot_pf | Trips when power factor falls below (or above) the configured limit.
40 | MP6 | Directional Active Power | D (ANSI 32) | 32 | Protection | kW | Protection cycle | prot_d | Directional active power protection for fault discrimination.
41 | MP6 | Reverse Reactive Power | RQ | 32Q-R | Protection | kVAr | Protection cycle | prot_rq | Trips on reverse reactive power flow.
42 | MP6 | Over Reactive Power | OQ | 32Q-O | Protection | kVAr | Protection cycle | prot_oq | Trips when reactive power demand exceeds configured limit.
43 | MP6 | Over Active Power | OP | 32P-O | Protection | kW | Protection cycle | prot_op | Trips when active power demand exceeds configured limit.
44 | MP6 | Under Active Power | UP | 32P-U | Protection | kW | Protection cycle | prot_up | Trips on loss-of-load (active power below threshold).
45 | MP6 | Second-stage Reverse Reactive | 2RQ | 32Q-R2 | Protection | kVAr | Protection cycle | prot_2rq | Escalated second stage of reverse reactive trip.
46 | MP7 | Earth-fault stage 1 | S(V) (ANSI 50G/51N) | 50G/51N | Protection | A | Protection cycle | prot_sv | First-stage earth-fault via residual current or voltage sensing.
47 | MP7 | Earth-fault stage 2 | S(V)2 | 50G-2 | Protection | A | Protection cycle | prot_sv2 | Faster second stage of earth-fault for severe faults.
48 | MP7 | Residual-Current (Earth Leakage) | R (ANSI 87N / Rc) | 87N/Rc | Protection | mA | Protection cycle | prot_r | True residual-current protection via ABB Ekip Rc module.

## Network & Protocol Plan
KINGSWALK — Network & Protocol Plan (proposal — client to confirm)
Every ABB Ekip trip unit and M4M 30 analyzer reaches the SCADA server over Ethernet via an Ekip Com IP gateway per main board. This sheet assigns a static IP, subnet, VLAN, protocol, port and Modbus Unit ID to every device. Addressing convention: 10.10.<MB>.0/24 per main board, where <MB> = 11, 21, 22, 23, 31, 41, 51, 52, 53. Anchor feeders (TS2) additionally expose IEC 61850 MMS on port 102. VLAN segregation: 10 SCADA device net, 20 Mgmt, 30 SCADA server-to-device.
Main Board | Device Role | DB Code | IP Address | Mask | Gateway | VLAN | Protocol | Port | Unit ID | Notes / Register Map
MB 1.1 | L3 gateway (site core, sub-interface) | — | 10.10.11.1 | /24 | — | VLAN 10 SCADA | — | — | — | Default gateway for the MB device subnet
MB 1.1 | Edge switch (managed L2) | — | 10.10.11.2 | /24 | 10.10.11.1 | VLAN 20 Mgmt | SNMPv3 | 161 | — | Per-MB PoE+ edge switch; trunks VLAN 10/20/30 to core
MB 1.1 | Ekip Com IP gateway (per-board head) | — | 10.10.11.10 | /24 | 10.10.11.1 | VLAN 10 SCADA | Modbus TCP | 502 | 1 | Aggregates the Ekip Link ring from all Tmax XT trip units on this MB; presents each trip unit as a Modbus TCP slave
MB 1.1 | M4M 30 analyzer — Main (TS2) incomer | — | 10.10.11.100 | /24 | 10.10.11.1 | VLAN 10 SCADA | Modbus TCP | 502 | 100 | Network analyzer on the Main supply incomer (MP2+MP3)
MB 1.1 | M4M 30 analyzer — Standby (TM3) incomer | — | 10.10.11.101 | /24 | 10.10.11.1 | VLAN 10 SCADA | Modbus TCP | 502 | 101 | Network analyzer on the Standby/generator incomer (MP2+MP3)
MB 1.1 | Outgoing DB (TM3) | DB-17 | 10.10.11.11 | /24 | 10.10.11.1 | VLAN 10 SCADA | Modbus TCP | 502 | 11 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 1.1 | Outgoing DB (TM3) | DB-17A | 10.10.11.12 | /24 | 10.10.11.1 | VLAN 10 SCADA | Modbus TCP | 502 | 12 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 1.1 | Outgoing DB (TM3) | DB-17B | 10.10.11.13 | /24 | 10.10.11.1 | VLAN 10 SCADA | Modbus TCP | 502 | 13 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 1.1 | Outgoing DB (TS2) | DB-18 | 10.10.11.14 | /24 | 10.10.11.1 | VLAN 10 SCADA | Modbus TCP + IEC 61850 | 502 / 102 | 14 | Ekip LSIG + Datalogger + IEC 61850 MMS (anchor)
MB 1.1 | Outgoing DB (TM3) | DB-19 | 10.10.11.15 | /24 | 10.10.11.1 | VLAN 10 SCADA | Modbus TCP | 502 | 15 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 1.1 | Outgoing DB (TM3) | DB-20/21 | 10.10.11.16 | /24 | 10.10.11.1 | VLAN 10 SCADA | Modbus TCP | 502 | 16 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 1.1 | Outgoing DB (TM3) | DB-22/23 | 10.10.11.17 | /24 | 10.10.11.1 | VLAN 10 SCADA | Modbus TCP | 502 | 17 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 1.1 | Outgoing DB (TM3) | DB-24 | 10.10.11.18 | /24 | 10.10.11.1 | VLAN 10 SCADA | Modbus TCP | 502 | 18 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 1.1 | Outgoing DB (TM3) | DB-24A | 10.10.11.19 | /24 | 10.10.11.1 | VLAN 10 SCADA | Modbus TCP | 502 | 19 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 1.1 | Outgoing DB (TM3) | DB-26 | 10.10.11.20 | /24 | 10.10.11.1 | VLAN 10 SCADA | Modbus TCP | 502 | 20 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.1 | L3 gateway (site core, sub-interface) | — | 10.10.21.1 | /24 | — | VLAN 10 SCADA | — | — | — | Default gateway for the MB device subnet
MB 2.1 | Edge switch (managed L2) | — | 10.10.21.2 | /24 | 10.10.21.1 | VLAN 20 Mgmt | SNMPv3 | 161 | — | Per-MB PoE+ edge switch; trunks VLAN 10/20/30 to core
MB 2.1 | Ekip Com IP gateway (per-board head) | — | 10.10.21.10 | /24 | 10.10.21.1 | VLAN 10 SCADA | Modbus TCP | 502 | 1 | Aggregates the Ekip Link ring from all Tmax XT trip units on this MB; presents each trip unit as a Modbus TCP slave
MB 2.1 | M4M 30 analyzer — Main (TS2) incomer | — | 10.10.21.100 | /24 | 10.10.21.1 | VLAN 10 SCADA | Modbus TCP | 502 | 100 | Network analyzer on the Main supply incomer (MP2+MP3)
MB 2.1 | M4M 30 analyzer — Standby (TM3) incomer | — | 10.10.21.101 | /24 | 10.10.21.1 | VLAN 10 SCADA | Modbus TCP | 502 | 101 | Network analyzer on the Standby/generator incomer (MP2+MP3)
MB 2.1 | Outgoing DB (TS2) | DB-05 | 10.10.21.11 | /24 | 10.10.21.1 | VLAN 10 SCADA | Modbus TCP + IEC 61850 | 502 / 102 | 11 | Ekip LSIG + Datalogger + IEC 61850 MMS (anchor)
MB 2.1 | Outgoing DB (TM3) | DB-08 | 10.10.21.12 | /24 | 10.10.21.1 | VLAN 10 SCADA | Modbus TCP | 502 | 12 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.1 | Outgoing DB (TM3) | DB-08A | 10.10.21.13 | /24 | 10.10.21.1 | VLAN 10 SCADA | Modbus TCP | 502 | 13 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.1 | Outgoing DB (TM3) | DB-09 | 10.10.21.14 | /24 | 10.10.21.1 | VLAN 10 SCADA | Modbus TCP | 502 | 14 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.1 | Outgoing DB (TM3) | DB-10 | 10.10.21.15 | /24 | 10.10.21.1 | VLAN 10 SCADA | Modbus TCP | 502 | 15 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.1 | Outgoing DB (TM3) | DB-11 | 10.10.21.16 | /24 | 10.10.21.1 | VLAN 10 SCADA | Modbus TCP | 502 | 16 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.1 | Outgoing DB (TM3) | DB-11A | 10.10.21.17 | /24 | 10.10.21.1 | VLAN 10 SCADA | Modbus TCP | 502 | 17 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.1 | Outgoing DB (TM3) | DB-12 | 10.10.21.18 | /24 | 10.10.21.1 | VLAN 10 SCADA | Modbus TCP | 502 | 18 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.2 | L3 gateway (site core, sub-interface) | — | 10.10.22.1 | /24 | — | VLAN 10 SCADA | — | — | — | Default gateway for the MB device subnet
MB 2.2 | Edge switch (managed L2) | — | 10.10.22.2 | /24 | 10.10.22.1 | VLAN 20 Mgmt | SNMPv3 | 161 | — | Per-MB PoE+ edge switch; trunks VLAN 10/20/30 to core
MB 2.2 | Ekip Com IP gateway (per-board head) | — | 10.10.22.10 | /24 | 10.10.22.1 | VLAN 10 SCADA | Modbus TCP | 502 | 1 | Aggregates the Ekip Link ring from all Tmax XT trip units on this MB; presents each trip unit as a Modbus TCP slave
MB 2.2 | M4M 30 analyzer — Main (TS2) incomer | — | 10.10.22.100 | /24 | 10.10.22.1 | VLAN 10 SCADA | Modbus TCP | 502 | 100 | Network analyzer on the Main supply incomer (MP2+MP3)
MB 2.2 | M4M 30 analyzer — Standby (TM3) incomer | — | 10.10.22.101 | /24 | 10.10.22.1 | VLAN 10 SCADA | Modbus TCP | 502 | 101 | Network analyzer on the Standby/generator incomer (MP2+MP3)
MB 2.2 | Outgoing DB (TM3) | DB-01 | 10.10.22.11 | /24 | 10.10.22.1 | VLAN 10 SCADA | Modbus TCP | 502 | 11 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.2 | Outgoing DB (TS2) | DB-01A | 10.10.22.12 | /24 | 10.10.22.1 | VLAN 10 SCADA | Modbus TCP + IEC 61850 | 502 / 102 | 12 | Ekip LSIG + Datalogger + IEC 61850 MMS (anchor)
MB 2.2 | Outgoing DB (TM3) | DB-01B | 10.10.22.13 | /24 | 10.10.22.1 | VLAN 10 SCADA | Modbus TCP | 502 | 13 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.2 | Outgoing DB (TM3) | DB-01C | 10.10.22.14 | /24 | 10.10.22.1 | VLAN 10 SCADA | Modbus TCP | 502 | 14 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.2 | Outgoing DB (TM3) | DB-01D | 10.10.22.15 | /24 | 10.10.22.1 | VLAN 10 SCADA | Modbus TCP | 502 | 15 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.2 | Outgoing DB (TM3) | DB-02 | 10.10.22.16 | /24 | 10.10.22.1 | VLAN 10 SCADA | Modbus TCP | 502 | 16 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.2 | Outgoing DB (TM3) | DB-03 | 10.10.22.17 | /24 | 10.10.22.1 | VLAN 10 SCADA | Modbus TCP | 502 | 17 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.2 | Outgoing DB (TM3) | DB-03A | 10.10.22.18 | /24 | 10.10.22.1 | VLAN 10 SCADA | Modbus TCP | 502 | 18 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.2 | Outgoing DB (TM3) | DB-04 | 10.10.22.19 | /24 | 10.10.22.1 | VLAN 10 SCADA | Modbus TCP | 502 | 19 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.3 | L3 gateway (site core, sub-interface) | — | 10.10.23.1 | /24 | — | VLAN 10 SCADA | — | — | — | Default gateway for the MB device subnet
MB 2.3 | Edge switch (managed L2) | — | 10.10.23.2 | /24 | 10.10.23.1 | VLAN 20 Mgmt | SNMPv3 | 161 | — | Per-MB PoE+ edge switch; trunks VLAN 10/20/30 to core
MB 2.3 | Ekip Com IP gateway (per-board head) | — | 10.10.23.10 | /24 | 10.10.23.1 | VLAN 10 SCADA | Modbus TCP | 502 | 1 | Aggregates the Ekip Link ring from all Tmax XT trip units on this MB; presents each trip unit as a Modbus TCP slave
MB 2.3 | M4M 30 analyzer — Main (TS2) incomer | — | 10.10.23.100 | /24 | 10.10.23.1 | VLAN 10 SCADA | Modbus TCP | 502 | 100 | Network analyzer on the Main supply incomer (MP2+MP3)
MB 2.3 | M4M 30 analyzer — Standby (TM3) incomer | — | 10.10.23.101 | /24 | 10.10.23.1 | VLAN 10 SCADA | Modbus TCP | 502 | 101 | Network analyzer on the Standby/generator incomer (MP2+MP3)
MB 2.3 | Outgoing DB (TM3) | DB-13/14 | 10.10.23.11 | /24 | 10.10.23.1 | VLAN 10 SCADA | Modbus TCP | 502 | 11 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.3 | Outgoing DB (TM3) | DB-15 | 10.10.23.12 | /24 | 10.10.23.1 | VLAN 10 SCADA | Modbus TCP | 502 | 12 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 2.3 | Outgoing DB (TM3) | DB-16 | 10.10.23.13 | /24 | 10.10.23.1 | VLAN 10 SCADA | Modbus TCP | 502 | 13 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | L3 gateway (site core, sub-interface) | — | 10.10.31.1 | /24 | — | VLAN 10 SCADA | — | — | — | Default gateway for the MB device subnet
MB 3.1 | Edge switch (managed L2) | — | 10.10.31.2 | /24 | 10.10.31.1 | VLAN 20 Mgmt | SNMPv3 | 161 | — | Per-MB PoE+ edge switch; trunks VLAN 10/20/30 to core
MB 3.1 | Ekip Com IP gateway (per-board head) | — | 10.10.31.10 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 1 | Aggregates the Ekip Link ring from all Tmax XT trip units on this MB; presents each trip unit as a Modbus TCP slave
MB 3.1 | M4M 30 analyzer — Main (TS2) incomer | — | 10.10.31.100 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 100 | Network analyzer on the Main supply incomer (MP2+MP3)
MB 3.1 | M4M 30 analyzer — Standby (TM3) incomer | — | 10.10.31.101 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 101 | Network analyzer on the Standby/generator incomer (MP2+MP3)
MB 3.1 | Outgoing DB (TM3) | DB-74 | 10.10.31.11 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 11 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-75 | 10.10.31.12 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 12 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-76 | 10.10.31.13 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 13 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-77 | 10.10.31.14 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 14 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-78 | 10.10.31.15 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 15 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-78A | 10.10.31.16 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 16 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-80 | 10.10.31.17 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 17 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-80A | 10.10.31.18 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 18 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-81 | 10.10.31.19 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 19 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-82 | 10.10.31.20 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 20 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-83 | 10.10.31.21 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 21 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-84 | 10.10.31.22 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 22 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-85 | 10.10.31.23 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 23 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-86 | 10.10.31.24 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 24 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-86A | 10.10.31.25 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 25 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-87 | 10.10.31.26 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 26 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-88 | 10.10.31.27 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 27 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-89 | 10.10.31.28 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 28 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-89A | 10.10.31.29 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 29 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-89B | 10.10.31.30 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 30 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-89C | 10.10.31.31 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 31 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-90 | 10.10.31.32 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 32 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-92 | 10.10.31.33 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 33 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 3.1 | Outgoing DB (TM3) | DB-SR1 | 10.10.31.34 | /24 | 10.10.31.1 | VLAN 10 SCADA | Modbus TCP | 502 | 34 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | L3 gateway (site core, sub-interface) | — | 10.10.41.1 | /24 | — | VLAN 10 SCADA | — | — | — | Default gateway for the MB device subnet
MB 4.1 | Edge switch (managed L2) | — | 10.10.41.2 | /24 | 10.10.41.1 | VLAN 20 Mgmt | SNMPv3 | 161 | — | Per-MB PoE+ edge switch; trunks VLAN 10/20/30 to core
MB 4.1 | Ekip Com IP gateway (per-board head) | — | 10.10.41.10 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 1 | Aggregates the Ekip Link ring from all Tmax XT trip units on this MB; presents each trip unit as a Modbus TCP slave
MB 4.1 | M4M 30 analyzer — Main (TS2) incomer | — | 10.10.41.100 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 100 | Network analyzer on the Main supply incomer (MP2+MP3)
MB 4.1 | M4M 30 analyzer — Standby (TM3) incomer | — | 10.10.41.101 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 101 | Network analyzer on the Standby/generator incomer (MP2+MP3)
MB 4.1 | Outgoing DB (TM3) | DB-46 | 10.10.41.11 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 11 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-47 | 10.10.41.12 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 12 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-48 | 10.10.41.13 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 13 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-48A | 10.10.41.14 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 14 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-48B | 10.10.41.15 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 15 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-48C | 10.10.41.16 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 16 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-52A | 10.10.41.17 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 17 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-53 | 10.10.41.18 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 18 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-54 | 10.10.41.19 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 19 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-55 | 10.10.41.20 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 20 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-57 | 10.10.41.21 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 21 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-58/59 | 10.10.41.22 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 22 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-60 | 10.10.41.23 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 23 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-62 | 10.10.41.24 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 24 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-64 | 10.10.41.25 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 25 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-66 | 10.10.41.26 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 26 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-66A | 10.10.41.27 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 27 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-67 | 10.10.41.28 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 28 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-67A | 10.10.41.29 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 29 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-68 | 10.10.41.30 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 30 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-69 | 10.10.41.31 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 31 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 4.1 | Outgoing DB (TM3) | DB-70 | 10.10.41.32 | /24 | 10.10.41.1 | VLAN 10 SCADA | Modbus TCP | 502 | 32 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.1 | L3 gateway (site core, sub-interface) | — | 10.10.51.1 | /24 | — | VLAN 10 SCADA | — | — | — | Default gateway for the MB device subnet
MB 5.1 | Edge switch (managed L2) | — | 10.10.51.2 | /24 | 10.10.51.1 | VLAN 20 Mgmt | SNMPv3 | 161 | — | Per-MB PoE+ edge switch; trunks VLAN 10/20/30 to core
MB 5.1 | Ekip Com IP gateway (per-board head) | — | 10.10.51.10 | /24 | 10.10.51.1 | VLAN 10 SCADA | Modbus TCP | 502 | 1 | Aggregates the Ekip Link ring from all Tmax XT trip units on this MB; presents each trip unit as a Modbus TCP slave
MB 5.1 | M4M 30 analyzer — Main (TS2) incomer | — | 10.10.51.100 | /24 | 10.10.51.1 | VLAN 10 SCADA | Modbus TCP | 502 | 100 | Network analyzer on the Main supply incomer (MP2+MP3)
MB 5.1 | M4M 30 analyzer — Standby (TM3) incomer | — | 10.10.51.101 | /24 | 10.10.51.1 | VLAN 10 SCADA | Modbus TCP | 502 | 101 | Network analyzer on the Standby/generator incomer (MP2+MP3)
MB 5.1 | Outgoing DB (TM3) | DB-38 | 10.10.51.11 | /24 | 10.10.51.1 | VLAN 10 SCADA | Modbus TCP | 502 | 11 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.1 | Outgoing DB (TM3) | DB-38A | 10.10.51.12 | /24 | 10.10.51.1 | VLAN 10 SCADA | Modbus TCP | 502 | 12 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.1 | Outgoing DB (TS1) | DB-39 | 10.10.51.13 | /24 | 10.10.51.1 | VLAN 10 SCADA | Modbus TCP | 502 | 13 | ⚠ TS1 anomaly — confirm protocol stack
MB 5.1 | Outgoing DB (TM3) | DB-FIRE | 10.10.51.14 | /24 | 10.10.51.1 | VLAN 10 SCADA | Modbus TCP | 502 | 14 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.1 | Outgoing DB (TM3) | DB-DOMESTIC | 10.10.51.15 | /24 | 10.10.51.1 | VLAN 10 SCADA | Modbus TCP | 502 | 15 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.1 | Outgoing DB (TM3) | DB-SR2 | 10.10.51.16 | /24 | 10.10.51.1 | VLAN 10 SCADA | Modbus TCP | 502 | 16 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.2 | L3 gateway (site core, sub-interface) | — | 10.10.52.1 | /24 | — | VLAN 10 SCADA | — | — | — | Default gateway for the MB device subnet
MB 5.2 | Edge switch (managed L2) | — | 10.10.52.2 | /24 | 10.10.52.1 | VLAN 20 Mgmt | SNMPv3 | 161 | — | Per-MB PoE+ edge switch; trunks VLAN 10/20/30 to core
MB 5.2 | Ekip Com IP gateway (per-board head) | — | 10.10.52.10 | /24 | 10.10.52.1 | VLAN 10 SCADA | Modbus TCP | 502 | 1 | Aggregates the Ekip Link ring from all Tmax XT trip units on this MB; presents each trip unit as a Modbus TCP slave
MB 5.2 | M4M 30 analyzer — Main (TS2) incomer | — | 10.10.52.100 | /24 | 10.10.52.1 | VLAN 10 SCADA | Modbus TCP | 502 | 100 | Network analyzer on the Main supply incomer (MP2+MP3)
MB 5.2 | M4M 30 analyzer — Standby (TM3) incomer | — | 10.10.52.101 | /24 | 10.10.52.1 | VLAN 10 SCADA | Modbus TCP | 502 | 101 | Network analyzer on the Standby/generator incomer (MP2+MP3)
MB 5.2 | Outgoing DB (TM3) | DB-40 | 10.10.52.11 | /24 | 10.10.52.1 | VLAN 10 SCADA | Modbus TCP | 502 | 11 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.2 | Outgoing DB (TM3) | DB-40A | 10.10.52.12 | /24 | 10.10.52.1 | VLAN 10 SCADA | Modbus TCP | 502 | 12 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.2 | Outgoing DB (TM3) | DB-41 | 10.10.52.13 | /24 | 10.10.52.1 | VLAN 10 SCADA | Modbus TCP | 502 | 13 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.2 | Outgoing DB (TM3) | DB-42 | 10.10.52.14 | /24 | 10.10.52.1 | VLAN 10 SCADA | Modbus TCP | 502 | 14 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.2 | Outgoing DB (TM3) | DB-43 | 10.10.52.15 | /24 | 10.10.52.1 | VLAN 10 SCADA | Modbus TCP | 502 | 15 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.2 | Outgoing DB (TM3) | DB-44 | 10.10.52.16 | /24 | 10.10.52.1 | VLAN 10 SCADA | Modbus TCP | 502 | 16 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.2 | Outgoing DB (TM3) | DB-44A | 10.10.52.17 | /24 | 10.10.52.1 | VLAN 10 SCADA | Modbus TCP | 502 | 17 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.2 | Outgoing DB (TM3) | DB-45 | 10.10.52.18 | /24 | 10.10.52.1 | VLAN 10 SCADA | Modbus TCP | 502 | 18 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.2 | Outgoing DB (TM3) | DB-45A | 10.10.52.19 | /24 | 10.10.52.1 | VLAN 10 SCADA | Modbus TCP | 502 | 19 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.2 | Outgoing DB (TM3) | DB-93 | 10.10.52.20 | /24 | 10.10.52.1 | VLAN 10 SCADA | Modbus TCP | 502 | 20 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.3 | L3 gateway (site core, sub-interface) | — | 10.10.53.1 | /24 | — | VLAN 10 SCADA | — | — | — | Default gateway for the MB device subnet
MB 5.3 | Edge switch (managed L2) | — | 10.10.53.2 | /24 | 10.10.53.1 | VLAN 20 Mgmt | SNMPv3 | 161 | — | Per-MB PoE+ edge switch; trunks VLAN 10/20/30 to core
MB 5.3 | Ekip Com IP gateway (per-board head) | — | 10.10.53.10 | /24 | 10.10.53.1 | VLAN 10 SCADA | Modbus TCP | 502 | 1 | Aggregates the Ekip Link ring from all Tmax XT trip units on this MB; presents each trip unit as a Modbus TCP slave
MB 5.3 | M4M 30 analyzer — Main (TS2) incomer | — | 10.10.53.100 | /24 | 10.10.53.1 | VLAN 10 SCADA | Modbus TCP | 502 | 100 | Network analyzer on the Main supply incomer (MP2+MP3)
MB 5.3 | M4M 30 analyzer — Standby (TM3) incomer | — | 10.10.53.101 | /24 | 10.10.53.1 | VLAN 10 SCADA | Modbus TCP | 502 | 101 | Network analyzer on the Standby/generator incomer (MP2+MP3)
MB 5.3 | Outgoing DB (TM3) | DB-27/28 | 10.10.53.11 | /24 | 10.10.53.1 | VLAN 10 SCADA | Modbus TCP | 502 | 11 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.3 | Outgoing DB (TM3) | DB-29 | 10.10.53.12 | /24 | 10.10.53.1 | VLAN 10 SCADA | Modbus TCP | 502 | 12 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.3 | Outgoing DB (TM3) | DB-30 | 10.10.53.13 | /24 | 10.10.53.1 | VLAN 10 SCADA | Modbus TCP | 502 | 13 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.3 | Outgoing DB (TM3) | DB-31 | 10.10.53.14 | /24 | 10.10.53.1 | VLAN 10 SCADA | Modbus TCP | 502 | 14 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.3 | Outgoing DB (TM3) | DB-32 | 10.10.53.15 | /24 | 10.10.53.1 | VLAN 10 SCADA | Modbus TCP | 502 | 15 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.3 | Outgoing DB (TM3) | DB-32A | 10.10.53.16 | /24 | 10.10.53.1 | VLAN 10 SCADA | Modbus TCP | 502 | 16 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.3 | Outgoing DB (TM3) | DB-33 | 10.10.53.17 | /24 | 10.10.53.1 | VLAN 10 SCADA | Modbus TCP | 502 | 17 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.3 | Outgoing DB (TM3) | DB-34 | 10.10.53.18 | /24 | 10.10.53.1 | VLAN 10 SCADA | Modbus TCP | 502 | 18 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.3 | Outgoing DB (TM3) | DB-36 | 10.10.53.19 | /24 | 10.10.53.1 | VLAN 10 SCADA | Modbus TCP | 502 | 19 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.3 | Outgoing DB (TM3) | DB-37 | 10.10.53.20 | /24 | 10.10.53.1 | VLAN 10 SCADA | Modbus TCP | 502 | 20 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.3 | Outgoing DB (TM3) | DB-SEC | 10.10.53.21 | /24 | 10.10.53.1 | VLAN 10 SCADA | Modbus TCP | 502 | 21 | ABB Ekip Datalogger (Modbus map ID 8xxx)
MB 5.3 | Outgoing DB (TM3) | DB-CM | 10.10.53.22 | /24 | 10.10.53.1 | VLAN 10 SCADA | Modbus TCP | 502 | 22 | ABB Ekip Datalogger (Modbus map ID 8xxx)
PER-MB SUBNET SUMMARY
MB | Subnet | Gateway | Edge Switch | Ekip Com GW | Usable Device Range | Devices
MB 1.1 | 10.10.11.0/24 | 10.10.11.1 | 10.10.11.2 | 10.10.11.10 | 10.10.11.11 – 10.10.11.20 | 10
MB 2.1 | 10.10.21.0/24 | 10.10.21.1 | 10.10.21.2 | 10.10.21.10 | 10.10.21.11 – 10.10.21.18 | 8
MB 2.2 | 10.10.22.0/24 | 10.10.22.1 | 10.10.22.2 | 10.10.22.10 | 10.10.22.11 – 10.10.22.19 | 9
MB 2.3 | 10.10.23.0/24 | 10.10.23.1 | 10.10.23.2 | 10.10.23.10 | 10.10.23.11 – 10.10.23.13 | 3
MB 3.1 | 10.10.31.0/24 | 10.10.31.1 | 10.10.31.2 | 10.10.31.10 | 10.10.31.11 – 10.10.31.34 | 24
MB 4.1 | 10.10.41.0/24 | 10.10.41.1 | 10.10.41.2 | 10.10.41.10 | 10.10.41.11 – 10.10.41.32 | 22
MB 5.1 | 10.10.51.0/24 | 10.10.51.1 | 10.10.51.2 | 10.10.51.10 | 10.10.51.11 – 10.10.51.16 | 6
MB 5.2 | 10.10.52.0/24 | 10.10.52.1 | 10.10.52.2 | 10.10.52.10 | 10.10.52.11 – 10.10.52.20 | 10
MB 5.3 | 10.10.53.0/24 | 10.10.53.1 | 10.10.53.2 | 10.10.53.10 | 10.10.53.11 – 10.10.53.22 | 12
TOTAL | [5 empty] | 104

## Gaps & Actions
KINGSWALK — Gaps, Open Items and Actions
All items requiring confirmation, decision, or engineering follow-up before procurement and final build. Each row links to a specific sheet in this workbook or a specific section of SPEC.md.
ID | Title | Description | Priority | Owner | Action | Status
GAP-01 | Serial-number placeholder on every DB on drawing 300 | Every outgoing on drawing 643.E.300 shows an empty 'serial' field — placeholder only. Cannot seed assets with real equipment serial numbers until on-site survey. | Medium | Site team | On-site survey to record actual ABB trip-unit serial numbers. | Open
GAP-02 | CT ratio source for non-metered tenants | Small tenants (60A TP feeds) are shown as 'DOL' rather than a CT ratio. Confirm that these feeds are intended to be read via the Ekip CT (no external CT), not a discrete metering CT. | Low | Consulting team | Confirm with engineer that DOL tenants use internal Ekip sensing. | Open
GAP-03 | Lighting group count per MB | Drawing 301 shows S1-6 / L1-6 / OL1-9 / P1-3 lighting groups. Drawings 302-309 have different counts per board and the full inventory has not been extracted yet. | Medium | Consulting team | Extract lighting group inventory from drawings 302-309. | Open
GAP-04 | Photocell addressing | Each MB has 3 photocells feeding remote inputs. Addressing scheme (per-photocell ID vs per-board ID) not yet defined. | Low | Consulting team | Define photocell naming convention; add to asset catalogue. | Open
GAP-05 | UPS assets (DB-SEC, DB-CM) | Security and Centre Management boards are backed by 10 kVA UPS units. UPS monitoring (battery health, runtime, bypass state) is a separate asset type not yet in the schema. | Medium | Consulting team | Add 'ups_unit' asset type; specify SNMP polling of UPS. | Open
GAP-06 | Electrified-fence feeder monitoring | Six electrified-fence feeders (EF-1..EF-6) are listed on drawing 300. Whether SCADA should monitor energizer state or just the feeder breaker is TBD. | Low | Security consultant | Scope energizer monitoring requirements with security integrator. | Open
GAP-07 | Tariff data for energy reports | Monthly reports require a tariff structure (bulk + tenant-split) to convert kWh into ZAR. Tariff schedule not yet provided. | High | Kingswalk management | Provide active tariff schedule and recharge rules. | Open
GAP-08 | POPIA responsibilities | System logs user actions and tenant consumption. POPIA information officer and data retention policy need to be defined. | High | Kingswalk management | Appoint information officer; define retention & consent flow. | Open
GAP-09 | Alarm escalation tree | Real-time alerts for critical events are specified but the escalation tree (who gets paged, when, via what channel) is not yet defined. | Medium | Kingswalk management | Define on-call rota and escalation rules per alarm class. | Open
GAP-10 | Backup & disaster recovery | Target uptime 99.9% requires automatic failover. Backup cadence, RPO/RTO and off-site backup location are TBD. | High | Watson Mattheus | Specify backup plan: PITR + nightly dumps + off-site. | Open
GAP-11 | Floor-plan SVG source | Interactive floor plan visualisation requires an SVG base layer. No SVG floor plan has been provided yet. | Medium | Architect | Request latest floor-plan SVG from architect. | Open
GAP-12 | WCAG compliance target | Non-functional requirement calls for WCAG-accessible design. Target level (AA vs AAA) and scope (core dashboard vs reports) not yet agreed. | Low | Kingswalk management | Confirm WCAG AA as baseline. | Open
GAP-13 | User role granularity | Spec lists Admin / Operator / Viewer. Whether additional roles (Tenant read-only access to their own DB data) are required is TBD. | Medium | Kingswalk management | Decide whether to expose a tenant-scoped view. | Open
GAP-14 | Language / localisation | Site is in South Africa. Interface language assumed English; Afrikaans and isiZulu not yet in scope but may be required for operator-facing screens. | Low | Kingswalk management | Confirm language requirements. | Open
GAP-15 | Device-level penetration test | Security audit and pen testing are in non-functional reqs but scope (code, network, device firmware) is not defined. | Medium | Watson Mattheus | Scope pen-test with a CREST-registered firm. | Open
GAP-16 | Breaker code TS1 used on DB-39 only | Drawing 307 shows DB-39 PICK n PAY with breaker code 'TS1', which does not appear in the SLD legend on any drawing. Likely typo for TS2 or TM3. | High | Consulting team | Clarify with drafter — amend drawing or confirm breaker family. | Open
GAP-17 | MP2 blanket assignment to all tenant feeds | Every outgoing on drawings 301–309 is tagged MP2 (Data Logger). MP3 (Network Analyzer), MP4–MP7 (protections) are only referenced in the legend, not actually assigned. | Medium | Watson Mattheus + Client | Client decision — may upgrade selected anchor feeds to add MP3. | Open
GAP-18 | DB naming discrepancy — DB-26 | Drawing 300 (overview) lists DB-26 as 'TOTALSPORTS' but drawing 301 (MB 1.1) shows DB-26 as 'EXACT'. One of the two sheets is out of date. | Medium | Consulting team | Reconcile with latest tenant schedule. | Open
GAP-19 | Protocol choice — Modbus TCP vs IEC 61850 | Default protocol is Modbus TCP port 502 via the Ekip Com IP gateway. Anchor feeders (TS2) are dual-stacked with IEC 61850 MMS port 102. Confirm whether IEC 61850 should be extended to all incomers or dropped entirely. | High | Watson Mattheus + Client | Client decision — drives Ekip Com licensing (LP3 vs LP2) and SCADA driver bundle. | Open
GAP-20 | IP scheme sign-off | Proposed scheme: 10.10.<MB>.0/24 per main board (MB octet = 11..53), gateway .1, edge switch .2, Ekip Com .10, per-outgoing .11+, M4M analyzers .100/.101. Confirm no overlap with existing Kingswalk estate network (guest wifi, CCTV, BMS). | High | Kingswalk IT + Consulting team | Get a clean RFC1918 range allocation letter from Kingswalk IT before commissioning. | Open
GAP-21 | VLAN segregation & structured cabling | SCADA device net on VLAN 10, management on VLAN 20, server-to-device on VLAN 30. Assumes CAT6 (or fibre) home-runs from each MB edge switch to a core switch in the control room, and assumes PoE+ available for the edge switches. | Medium | Consulting team | Issue as scope line on the structured-cabling subcontract. Specify fibre where run >90 m. | Open

## Breaker MP Schedule
KINGSWALK — Breaker Measuring-Package Schedule
Every incomer and outgoing breaker across MB 1.1 – MB 5.3 with its assigned Measuring Package and the ordered list of functions that package captures. Data source: per-MB drawings 643.E.301–309.
MB | Drawing | Role | Label / DB Code | Tenant / Name | Breaker Code | Rating (A) | Poles | MP | MP Functions (ordered)
MB 1.1 | 643.E.301 | Incomer | MB-1.1-INCOMER |  | TS2 | 1600 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.1 | 643.E.302 | Incomer | MB-2.1-INCOMER |  | TS2 | 1600 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.2 | 643.E.303 | Incomer | MB-2.2-INCOMER |  | TS2 | 1600 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.3 | 643.E.304 | Incomer | MB-2.3-INCOMER |  | TS2 | 800 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Incomer | MB-3.1-INCOMER |  | TS2 | 2000 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Incomer | MB-4.1-INCOMER |  | TS2 | 2000 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.1 | 643.E.307 | Incomer | MB-5.1-INCOMER |  | TS2 | 1600 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.2 | 643.E.308 | Incomer | MB-5.2-INCOMER |  | TS2 | 1600 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.3 | 643.E.309 | Incomer | MB-5.3-INCOMER |  | TS2 | 600 | TP | MP4 | Phase-to-neutral voltage • Line currents • Power factor • Mains-loss event counter • Auto-transfer state • Running hours on essential
MB 1.1 | 643.E.301 | Outgoing | DB-17 | PEP CELL | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 1.1 | 643.E.301 | Outgoing | DB-17A | LL KING PIE | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 1.1 | 643.E.301 | Outgoing | DB-17B | PIE MR PRICE CELL | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 1.1 | 643.E.301 | Outgoing | DB-18 | SHOPRITE | TS2 | 800 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 1.1 | 643.E.301 | Outgoing | DB-19 | TRUWORTHS | TM3 | 200 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 1.1 | 643.E.301 | Outgoing | DB-20/21 | THS IDENTITY / SYNC | TM3 | 200 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 1.1 | 643.E.301 | Outgoing | DB-22/23 | JET | TM3 | 200 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 1.1 | 643.E.301 | Outgoing | DB-24 | SPORTSCENE | TM3 | 120 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 1.1 | 643.E.301 | Outgoing | DB-24A |  | TM3 | 120 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 1.1 | 643.E.301 | Outgoing | DB-26 | EXACT | TM3 | 120 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.1 | 643.E.302 | Outgoing | DB-05 |  | TS2 | 600 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.1 | 643.E.302 | Outgoing | DB-08 |  | TM3 | 150 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.1 | 643.E.302 | Outgoing | DB-08A |  | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.1 | 643.E.302 | Outgoing | DB-09 |  | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.1 | 643.E.302 | Outgoing | DB-10 |  | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.1 | 643.E.302 | Outgoing | DB-11 |  | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.1 | 643.E.302 | Outgoing | DB-11A |  | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.1 | 643.E.302 | Outgoing | DB-12 |  | TM3 | 120 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.2 | 643.E.303 | Outgoing | DB-01 | VACANT | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.2 | 643.E.303 | Outgoing | DB-01A | T WATLOO | TS2 | 200 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.2 | 643.E.303 | Outgoing | DB-01B | KINGSLEY BEVERAGES | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.2 | 643.E.303 | Outgoing | DB-01C | KIT KAT | TM3 | 120 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.2 | 643.E.303 | Outgoing | DB-01D | CAPITEC ATM | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.2 | 643.E.303 | Outgoing | DB-02 | VACANT | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.2 | 643.E.303 | Outgoing | DB-03 | MAX BOX | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.2 | 643.E.303 | Outgoing | DB-03A | ACKERMANS CONNECT | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.2 | 643.E.303 | Outgoing | DB-04 |  | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.3 | 643.E.304 | Outgoing | DB-13/14 | VACANT | TM3 | 200 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.3 | 643.E.304 | Outgoing | DB-15 | CLICKS | TM3 | 200 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 2.3 | 643.E.304 | Outgoing | DB-16 | S SHOPRITE LIQUOR | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-74 | SPUR | TM3 | 150 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-75 | KFC | TM3 | 150 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-76 | STEERS & DEBONAIRS | TM3 | 150 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-77 | RS ROCOMAMA'S | TM3 | 150 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-78 | CONVERSE | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-78A | CAPITEC ATM | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-80 | ATM VACANT | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-80A | SPECSAVERS | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-81 | ERS VACANT | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-82 | SKIPPER BAR | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-83 | VACANT | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-84 | DUNNS | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-85 | VICTORY LAB | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-86 | VACANT | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-86A | POWER FASHION | TM3 | 120 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-87 | VACANT | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-88 | VACANT | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-89 | VACANT | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-89A | NEDBANK ATM | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-89B | CAKE ZONE | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-89C | VACANT | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-90 |  | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-92 | ABS | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 3.1 | 643.E.305 | Outgoing | DB-SR1 | TORE ROOM 1 | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-46 | FNB | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-47 | STANDARD BANK | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-48 | ANK VACANT | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-48A | ATM | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-48B | VACANT | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-48C | VACANT | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-52A | PEP HOME | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-53 | OME MR PRICE & KIDS | TM3 | 200 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-54 | & KIDS TEKKIE TOWN | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-55 | VACANT | TM3 | 120 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-57 | ACKERMANS | TM3 | 200 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-58/59 | STUDIO 88 | TM3 | 120 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-60 | THE FIX | TM3 | 120 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-62 | SIDE STEP | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-64 | VACANT | TM3 | 200 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-66 | POLO | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-66A | STERNS / VACANT | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-67 | PEDRO | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-67A | VACANT | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-68 | ROMANS PIZZA | TM3 | 150 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-69 | HUNGRY LION | TM3 | 150 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 4.1 | 643.E.306 | Outgoing | DB-70 |  | TM3 | 150 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.1 | 643.E.307 | Outgoing | DB-38 |  | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.1 | 643.E.307 | Outgoing | DB-38A |  | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.1 | 643.E.307 | Outgoing | DB-39 |  | TS1 | 200 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.1 | 643.E.307 | Outgoing | DB-FIRE |  | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.1 | 643.E.307 | Outgoing | DB-DOMESTIC |  | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.1 | 643.E.307 | Outgoing | DB-SR2 |  | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.2 | 643.E.308 | Outgoing | DB-40 | VACANT | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.2 | 643.E.308 | Outgoing | DB-40A | T VACANT | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.2 | 643.E.308 | Outgoing | DB-41 | T TORGA OPTICAL | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.2 | 643.E.308 | Outgoing | DB-42 | AMERICAN SWISS | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.2 | 643.E.308 | Outgoing | DB-43 | OLD MUTUAL | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.2 | 643.E.308 | Outgoing | DB-44 | CAPITEC | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.2 | 643.E.308 | Outgoing | DB-44A | MOJO | TM3 | 120 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.2 | 643.E.308 | Outgoing | DB-45 | BRADLOWS | TM3 | 120 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.2 | 643.E.308 | Outgoing | DB-45A |  | TM3 | 120 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.2 | 643.E.308 | Outgoing | DB-93 | CASHBUILD | TM3 | 200 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.3 | 643.E.309 | Outgoing | DB-27/28 | TOTALSPORTS | TM3 | 120 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.3 | 643.E.309 | Outgoing | DB-29 | S VACANT | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.3 | 643.E.309 | Outgoing | DB-30 | T LEGIT | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.3 | 643.E.309 | Outgoing | DB-31 | JOHN GRAIG | TM3 | 100 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.3 | 643.E.309 | Outgoing | DB-32 | VACANT | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.3 | 643.E.309 | Outgoing | DB-32A | CODE | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.3 | 643.E.309 | Outgoing | DB-33 | REFINERY | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.3 | 643.E.309 | Outgoing | DB-34 | VOLPES | TM3 | 120 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.3 | 643.E.309 | Outgoing | DB-36 | ARTHUR FORD | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.3 | 643.E.309 | Outgoing | DB-37 | DISCHEM | TM3 | 200 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.3 | 643.E.309 | Outgoing | DB-SEC | SECURITY | TM3 | 60 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents
MB 5.3 | 643.E.309 | Outgoing | DB-CM |  | TM3 | 80 | TP | MP2 | Phase-to-phase voltage • Phase-to-neutral voltage • Frequency • Active power (P) • Reactive power (Q) • Apparent power (S) • Power factor • Line currents